## Signals
Intesis MAPS Excel signals file
PROJECT_NAME | Project1
Intesis MAPS Version | 1.2.26.0
Internal Protocol | KNX
External Protocol | Modbus Master
Timestamp | 2026-01-23
# | Active | Description | DPT | Group Address | Additional Addresses | U | T | Ri | W | R | Priority | # | Device | # Slave | Base | Read Func | Write Func | Data Length | Format | ByteOrder | Address | Bit | # Bits | Deadband | Conv. Id | Conversions
1 | True | Comm Error Device 0 | 1.005: alarm | 0/0/100 |  |  | T |  |  | R | 3: Low | 1 | RTU // Port B // Device 0 | 10 | 0-based | - | - | - | - | - | - | - | - | - |  | -
2 | True | Comm Error Device 1 | 1.005: alarm | 0/0/101 |  |  | T |  |  | R | 3: Low | 2 | RTU // Port B // Device 1 | 11 | 0-based | - | - | - | - | - | - | - | - | - |  | -
3 | True | Comm Error Device 2 | 1.005: alarm | 0/0/102 |  |  | T |  |  | R | 3: Low | 3 | RTU // Port B // Device 2 | 12 | 0-based | - | - | - | - | - | - | - | - | - |  | -
4 | True | On_Off_R | 1.001: switch | 0/0/1 |  |  | T |  |  | R | 3: Low | 4 | RTU // Port B // Device 0 | 10 | 0-based | 1: Read Coils | - | 1 | - | - | 0 | - | - | 0 |  | -
5 | True | On_Off_W | 1.001: switch | 0/0/2 |  | U |  |  | W |  | 3: Low | 5 | RTU // Port B // Device 0 | 10 | 0-based | - | 5: Write Single Coil | 1 | - | - | 1 | - | - | 0 |  | -
6 | True | On_Off_RW | 1.001: switch | 0/0/3 |  | U | T |  | W | R | 3: Low | 6 | RTU // Port B // Device 0 | 10 | 0-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2 | - | - | 0 |  | -
7 | True | Temp_R | 9.001: temperature (ºC) | 0/0/4 |  |  | T |  |  | R | 3: Low | 7 | RTU // Port B // Device 1 | 11 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 0 | - | - | 0 |  | -
8 | True | Temp_W | 9.001: temperature (ºC) | 0/0/5 |  | U |  |  | W |  | 3: Low | 8 | RTU // Port B // Device 1 | 11 | 0-based | - | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 1 | - | - | 0 |  | -
9 | True | Temp_RW | 9.001: temperature (ºC) | 0/0/6 |  | U | T |  | W | R | 3: Low | 9 | RTU // Port B // Device 1 | 11 | 0-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 2 | - | - | 0 |  | -
10 | True | Counter_R | 5.010: counter pulses (0..255) | 0/0/7 |  |  | T |  |  | R | 3: Low | 10 | RTU // Port B // Device 2 | 12 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 0 | - | - | 0 |  | -
11 | True | Counter_W | 5.010: counter pulses (0..255) | 0/0/8 |  | U |  |  | W |  | 3: Low | 11 | RTU // Port B // Device 2 | 12 | 0-based | - | 16: Write Multiple Registers | 32 | 0: Unsigned | 0: Big Endian | 2 | - | - | 0 |  | -
12 | True | Counter_RW | 5.010: counter pulses (0..255) | 0/0/9 |  | U | T |  | W | R | 3: Low | 12 | RTU // Port B // Device 2 | 12 | 0-based | 3: Read Holding Registers | 16: Write Multiple Registers | 32 | 0: Unsigned | 0: Big Endian | 4 | - | - | 0 |  | -
13 | True | Comm Error RTU Port B - GE_EPM2200_Meter_a | 1.001: switch | 0/0/103 | [6 empty] | 3: Low | 13 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | - | - | 1 | - | - | - | - | - | - |  | -
14 | True | Watts 3-Ph total | 14.056: power (W) | 0/0/3 |  |  | T |  |  | R | 3: Low | 14 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 900 | - | - | 0 |  | -
15 | True | VARs 3-Ph total | 14.x: (4-byte, Float Value) | 0/0/4 |  |  | T |  |  | R | 3: Low | 15 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 902 | - | - | 0 |  | -
16 | True | VAs 3-Ph total | 14.x: (4-byte, Float Value) | 0/0/5 |  |  | T |  |  | R | 3: Low | 16 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 904 | - | - | 0 |  | -
17 | True | Volts A-N | 14.028: electric potential difference (V) | 0/0/6 |  |  | T |  |  | R | 3: Low | 17 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1000 | - | - | 0 |  | -
18 | True | Volts B-N | 14.028: electric potential difference (V) | 0/0/7 |  |  | T |  |  | R | 3: Low | 18 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1002 | - | - | 0 |  | -
19 | True | Volts C-N | 14.028: electric potential difference (V) | 0/0/8 |  |  | T |  |  | R | 3: Low | 19 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1004 | - | - | 0 |  | -
20 | True | Volts A-B | 14.028: electric potential difference (V) | 0/0/9 |  |  | T |  |  | R | 3: Low | 20 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1006 | - | - | 0 |  | -
21 | True | Volts B-C | 14.028: electric potential difference (V) | 0/0/10 |  |  | T |  |  | R | 3: Low | 21 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1008 | - | - | 0 |  | -
22 | True | Volts C-A | 14.028: electric potential difference (V) | 0/0/11 |  |  | T |  |  | R | 3: Low | 22 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1010 | - | - | 0 |  | -
23 | True | Amps A | 14.019: electric current (A) | 0/0/12 |  |  | T |  |  | R | 3: Low | 23 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1012 | - | - | 0 |  | -
24 | True | Amps B | 14.019: electric current (A) | 0/0/13 |  |  | T |  |  | R | 3: Low | 24 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1014 | - | - | 0 |  | -
25 | True | Amps C | 14.019: electric current (A) | 0/0/14 |  |  | T |  |  | R | 3: Low | 25 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1016 | - | - | 0 |  | -
26 | True | Watts 3-Ph total * | 14.056: power (W) | 0/0/15 |  |  | T |  |  | R | 3: Low | 26 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1018 | - | - | 0 |  | -
27 | True | VARs 3-Ph total * | 14.x: (4-byte, Float Value) | 0/0/16 |  |  | T |  |  | R | 3: Low | 27 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1020 | - | - | 0 |  | -
28 | True | VAs 3-Ph total * | 14.x: (4-byte, Float Value) | 0/0/17 |  |  | T |  |  | R | 3: Low | 28 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1022 | - | - | 0 |  | -
29 | True | Power Factor 3-Ph total | 14.057: power factor (cos) | 0/0/18 |  |  | T |  |  | R | 3: Low | 29 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1024 | - | - | 0 |  | -
30 | True | Frequency | 14.033: frequency (Hz) | 0/0/19 |  |  | T |  |  | R | 3: Low | 30 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1026 | - | - | 0 |  | -
31 | True | Neutral Current | 14.019: electric current (A) | 0/0/20 |  |  | T |  |  | R | 3: Low | 31 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1028 | - | - | 0 |  | -
32 | True | W-hours Received | 13.x: (4-byte, Signed Value) | 0/0/21 |  |  | T |  |  | R | 3: Low | 32 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1100 | - | - | 0 |  | -
33 | True | W-hours Delivered | 13.x: (4-byte, Signed Value) | 0/0/22 |  |  | T |  |  | R | 3: Low | 33 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1102 | - | - | 0 |  | -
34 | True | W-hours Net | 13.x: (4-byte, Signed Value) | 0/0/23 |  |  | T |  |  | R | 3: Low | 34 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1104 | - | - | 0 |  | -
35 | True | W-hours Total | 13.x: (4-byte, Signed Value) | 0/0/24 |  |  | T |  |  | R | 3: Low | 35 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1106 | - | - | 0 |  | -
36 | True | VAR-hours Positive | 13.x: (4-byte, Signed Value) | 0/0/25 |  |  | T |  |  | R | 3: Low | 36 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1108 | - | - | 0 |  | -
37 | True | VAR-hours Negative | 13.x: (4-byte, Signed Value) | 0/0/26 |  |  | T |  |  | R | 3: Low | 37 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1110 | - | - | 0 |  | -
38 | True | VAR-hours Net | 13.x: (4-byte, Signed Value) | 0/0/27 |  |  | T |  |  | R | 3: Low | 38 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1112 | - | - | 0 |  | -
39 | True | VAR-hours Total | 13.x: (4-byte, Signed Value) | 0/0/28 |  |  | T |  |  | R | 3: Low | 39 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1114 | - | - | 0 |  | -
40 | True | VA-hours Total | 13.x: (4-byte, Signed Value) | 0/0/29 |  |  | T |  |  | R | 3: Low | 40 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1116 | - | - | 0 |  | -
41 | True | Amps A Average | 14.019: electric current (A) | 0/0/30 |  |  | T |  |  | R | 3: Low | 41 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2000 | - | - | 0 |  | -
42 | True | Amps B Average | 14.019: electric current (A) | 0/0/31 |  |  | T |  |  | R | 3: Low | 42 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2002 | - | - | 0 |  | -
43 | True | Amps C Average | 14.019: electric current (A) | 0/0/32 |  |  | T |  |  | R | 3: Low | 43 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2004 | - | - | 0 |  | -
44 | True | Positive Watts 3-Ph average | 14.056: power (W) | 0/0/33 |  |  | T |  |  | R | 3: Low | 44 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2006 | - | - | 0 |  | -
45 | True | Positive VARs 3-Ph average | 14.x: (4-byte, Float Value) | 0/0/34 |  |  | T |  |  | R | 3: Low | 45 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2008 | - | - | 0 |  | -
46 | True | Negative Watts 3-Ph average | 14.056: power (W) | 0/0/35 |  |  | T |  |  | R | 3: Low | 46 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2010 | - | - | 0 |  | -
47 | True | Negative VARs 3-Ph average | 14.x: (4-byte, Float Value) | 0/0/36 |  |  | T |  |  | R | 3: Low | 47 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2012 | - | - | 0 |  | -
48 | True | VAs 3-Ph Average | 14.x: (4-byte, Float Value) | 0/0/37 |  |  | T |  |  | R | 3: Low | 48 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2014 | - | - | 0 |  | -
49 | True | Positive PF 3-Ph average | 14.057: power factor (cos) | 0/0/38 |  |  | T |  |  | R | 3: Low | 49 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2016 | - | - | 0 |  | -
50 | True | Negative PF 3-PF average | 14.057: power factor (cos) | 0/0/39 |  |  | T |  |  | R | 3: Low | 50 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2018 | - | - | 0 |  | -
51 | True | Volts A-N Minimum | 14.028: electric potential difference (V) | 0/0/40 |  |  | T |  |  | R | 3: Low | 51 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3000 | - | - | 0 |  | -
52 | True | Volts B-N Minimum | 14.028: electric potential difference (V) | 0/0/41 |  |  | T |  |  | R | 3: Low | 52 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3002 | - | - | 0 |  | -
53 | True | Volts C-N Minimum | 14.028: electric potential difference (V) | 0/0/42 |  |  | T |  |  | R | 3: Low | 53 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3004 | - | - | 0 |  | -
54 | True | Volts A-B Minimum | 14.028: electric potential difference (V) | 0/0/43 |  |  | T |  |  | R | 3: Low | 54 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3006 | - | - | 0 |  | -
55 | True | Volts B-C Minimum | 14.028: electric potential difference (V) | 0/0/44 |  |  | T |  |  | R | 3: Low | 55 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3008 | - | - | 0 |  | -
56 | True | Volts C-A Minimum | 14.028: electric potential difference (V) | 0/0/45 |  |  | T |  |  | R | 3: Low | 56 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3010 | - | - | 0 |  | -
57 | True | Amps A Minimum Avg demand | 14.019: electric current (A) | 0/0/46 |  |  | T |  |  | R | 3: Low | 57 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3012 | - | - | 0 |  | -
58 | True | Amps B Minimum Avg demand | 14.019: electric current (A) | 0/0/47 |  |  | T |  |  | R | 3: Low | 58 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3014 | - | - | 0 |  | -
59 | True | Amps C Minimum Avg demand | 14.019: electric current (A) | 0/0/48 |  |  | T |  |  | R | 3: Low | 59 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3016 | - | - | 0 |  | -
60 | True | Positive Watts 3-Ph Minimum Ave | 14.056: power (W) | 0/0/49 |  |  | T |  |  | R | 3: Low | 60 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3018 | - | - | 0 |  | -
61 | True | Positive VARs 3-Ph Minimum Aver | 14.x: (4-byte, Float Value) | 0/0/50 |  |  | T |  |  | R | 3: Low | 61 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3020 | - | - | 0 |  | -
62 | True | Negative Watts 3-Ph Minimum Ave | 14.056: power (W) | 0/0/51 |  |  | T |  |  | R | 3: Low | 62 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3022 | - | - | 0 |  | -
63 | True | Negative VARs 3-Ph Minimum Aver | 14.x: (4-byte, Float Value) | 0/0/52 |  |  | T |  |  | R | 3: Low | 63 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3024 | - | - | 0 |  | -
64 | True | VAs 3-Ph Minimum Avg Demand | 14.x: (4-byte, Float Value) | 0/0/53 |  |  | T |  |  | R | 3: Low | 64 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3026 | - | - | 0 |  | -
65 | True | Positive Power Factor 3-Ph Mini | 14.057: power factor (cos) | 0/0/54 |  |  | T |  |  | R | 3: Low | 65 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3028 | - | - | 0 |  | -
66 | True | Negative Power Factor 3-Ph Mini | 14.057: power factor (cos) | 0/0/55 |  |  | T |  |  | R | 3: Low | 66 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3030 | - | - | 0 |  | -
67 | True | Frequency Minimum | 14.033: frequency (Hz) | 0/0/56 |  |  | T |  |  | R | 3: Low | 67 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3032 | - | - | 0 |  | -
68 | True | Volts A-N Maximum | 14.028: electric potential difference (V) | 0/0/57 |  |  | T |  |  | R | 3: Low | 68 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3100 | - | - | 0 |  | -
69 | True | Volts B-N Maximum | 14.028: electric potential difference (V) | 0/0/58 |  |  | T |  |  | R | 3: Low | 69 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3102 | - | - | 0 |  | -
70 | True | Volts C-N Maximum | 14.028: electric potential difference (V) | 0/0/59 |  |  | T |  |  | R | 3: Low | 70 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3104 | - | - | 0 |  | -
71 | True | Volts A-B Maximum | 14.028: electric potential difference (V) | 0/0/60 |  |  | T |  |  | R | 3: Low | 71 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3106 | - | - | 0 |  | -
72 | True | Volts B-C Maximum | 14.028: electric potential difference (V) | 0/0/61 |  |  | T |  |  | R | 3: Low | 72 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3108 | - | - | 0 |  | -
73 | True | Volts C-A Maximum | 14.028: electric potential difference (V) | 0/0/62 |  |  | T |  |  | R | 3: Low | 73 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3110 | - | - | 0 |  | -
74 | True | Amps A Maximum Avg demand | 14.019: electric current (A) | 0/0/63 |  |  | T |  |  | R | 3: Low | 74 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3112 | - | - | 0 |  | -
75 | True | Amps B Maximum Avg demand | 14.019: electric current (A) | 0/0/64 |  |  | T |  |  | R | 3: Low | 75 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3114 | - | - | 0 |  | -
76 | True | Amps C Maximum Avg demand | 14.019: electric current (A) | 0/0/65 |  |  | T |  |  | R | 3: Low | 76 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3116 | - | - | 0 |  | -
77 | True | Positive Watts 3-Ph Maximum Avg | 14.056: power (W) | 0/0/66 |  |  | T |  |  | R | 3: Low | 77 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3118 | - | - | 0 |  | -
78 | True | Positive VARs 3-Ph Maximum Avg | 14.x: (4-byte, Float Value) | 0/0/67 |  |  | T |  |  | R | 3: Low | 78 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3120 | - | - | 0 |  | -
79 | True | Negative Watts 3-Ph Maximum Avg | 14.056: power (W) | 0/0/68 |  |  | T |  |  | R | 3: Low | 79 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3122 | - | - | 0 |  | -
80 | True | Negative VARs 3-Ph Maximum Avg | 14.x: (4-byte, Float Value) | 0/0/69 |  |  | T |  |  | R | 3: Low | 80 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3124 | - | - | 0 |  | -
81 | True | VAs 3-Ph Maximum Avg Demand | 14.x: (4-byte, Float Value) | 0/0/70 |  |  | T |  |  | R | 3: Low | 81 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3126 | - | - | 0 |  | -
82 | True | Positive Power Factor 3-Ph Maxi | 14.057: power factor (cos) | 0/0/71 |  |  | T |  |  | R | 3: Low | 82 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3128 | - | - | 0 |  | -
83 | True | Negative Power Factor 3-Ph Maxi | 14.057: power factor (cos) | 0/0/72 |  |  | T |  |  | R | 3: Low | 83 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3130 | - | - | 0 |  | -
84 | True | Frequency Maximum | 14.033: frequency (Hz) | 0/0/73 |  |  | T |  |  | R | 3: Low | 84 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3132 | - | - | 0 |  | -
85 | True | Phase A Current | 14.055: phase angle (º) | 0/0/74 |  |  | T |  |  | R | 3: Low | 85 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4100 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
86 | True | Phase B Current | 14.055: phase angle (º) | 0/0/75 |  |  | T |  |  | R | 3: Low | 86 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4101 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
87 | True | Phase C Current | 14.055: phase angle (º) | 0/0/76 |  |  | T |  |  | R | 3: Low | 87 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4102 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
88 | True | Angle Volts A-B | 14.055: phase angle (º) | 0/0/77 |  |  | T |  |  | R | 3: Low | 88 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4103 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
89 | True | Angle Volts B-C | 14.055: phase angle (º) | 0/0/78 |  |  | T |  |  | R | 3: Low | 89 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4104 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
90 | True | Angle Volts C-A | 14.055: phase angle (º) | 0/0/79 |  |  | T |  |  | R | 3: Low | 90 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4105 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
91 | True | Meter Status | 7.x: (2-byte, Unsigned Value) | 0/0/80 |  |  | T |  |  | R | 3: Low | 91 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 5000 | - | - | 0 |  | -
92 | True | Time Since Reset | 12.x: (4-byte, Unsigned Value) | 0/0/81 |  |  | T |  |  | R | 3: Low | 92 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 5002 | - | - | 0 |  | -
93 | True | System Sanity Indicator | 7.x: (2-byte, Unsigned Value) | 0/0/82 |  |  | T |  |  | R | 3: Low | 93 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40001 | - | - | 0 |  | -
94 | True | Volts A-N * | 14.028: electric potential difference (V) | 0/0/83 |  |  | T |  |  | R | 3: Low | 94 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40002 | - | - | 0 |  | -
95 | True | Volts B-N * | 14.028: electric potential difference (V) | 0/0/84 |  |  | T |  |  | R | 3: Low | 95 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40003 | - | - | 0 |  | -
96 | True | Volts C-N * | 14.028: electric potential difference (V) | 0/0/85 |  |  | T |  |  | R | 3: Low | 96 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40004 | - | - | 0 |  | -
97 | True | Amps A * | 14.019: electric current (A) | 0/0/86 |  |  | T |  |  | R | 3: Low | 97 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40005 | - | - | 0 |  | -
98 | True | Amps B * | 14.019: electric current (A) | 0/0/87 |  |  | T |  |  | R | 3: Low | 98 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40006 | - | - | 0 |  | -
99 | True | Amps C * | 14.019: electric current (A) | 0/0/88 |  |  | T |  |  | R | 3: Low | 99 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40007 | - | - | 0 |  | -
100 | True | Watts 3-Ph total * | 14.056: power (W) | 0/0/89 |  |  | T |  |  | R | 3: Low | 100 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40008 | - | - | 0 |  | -
101 | True | VARs 3-Ph total * | 7.x: (2-byte, Unsigned Value) | 0/0/90 |  |  | T |  |  | R | 3: Low | 101 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40009 | - | - | 0 |  | -
102 | True | VAs 3-Ph total * | 7.x: (2-byte, Unsigned Value) | 0/0/91 |  |  | T |  |  | R | 3: Low | 102 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40010 | - | - | 0 |  | -
103 | True | Power Factor 3-Ph Total | 14.057: power factor (cos) | 0/0/92 |  |  | T |  |  | R | 3: Low | 103 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40011 | - | - | 0 |  | -
104 | True | Frequency * | 14.033: frequency (Hz) | 0/0/93 |  |  | T |  |  | R | 3: Low | 104 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40012 | - | - | 0 |  | -
105 | True | Volts A-B * | 14.028: electric potential difference (V) | 0/0/94 |  |  | T |  |  | R | 3: Low | 105 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40013 | - | - | 0 |  | -
106 | True | Volts B-C * | 14.028: electric potential difference (V) | 0/0/95 |  |  | T |  |  | R | 3: Low | 106 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40014 | - | - | 0 |  | -
107 | True | Volts C-A * | 14.028: electric potential difference (V) | 0/0/96 |  |  | T |  |  | R | 3: Low | 107 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40015 | - | - | 0 |  | -
108 | True | CT numerator | 7.x: (2-byte, Unsigned Value) | 0/0/97 |  |  | T |  |  | R | 3: Low | 108 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40016 | - | - | 0 |  | -
109 | True | CT multiplier | 7.x: (2-byte, Unsigned Value) | 0/0/98 |  |  | T |  |  | R | 3: Low | 109 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40017 | - | - | 0 |  | -
110 | True | CT denominator | 7.x: (2-byte, Unsigned Value) | 0/0/99 |  |  | T |  |  | R | 3: Low | 110 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40018 | - | - | 0 |  | -
111 | True | PT numerator | 7.x: (2-byte, Unsigned Value) | 0/0/100 |  |  | T |  |  | R | 3: Low | 111 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40019 | - | - | 0 |  | -
112 | True | PT multiplier | 7.x: (2-byte, Unsigned Value) | 0/0/101 |  |  | T |  |  | R | 3: Low | 112 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40020 | - | - | 0 |  | -
113 | True | PT denominator | 7.x: (2-byte, Unsigned Value) | 0/0/102 |  |  | T |  |  | R | 3: Low | 113 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40021 | - | - | 0 |  | -
114 | True | W-hours Positive | 13.010: active energy (Wh) | 0/0/103 |  |  | T |  |  | R | 3: Low | 114 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 40022 | - | - | 0 |  | -
115 | True | W-hours Negative | 13.010: active energy (Wh) | 0/0/104 |  |  | T |  |  | R | 3: Low | 115 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 40024 | - | - | 0 |  | -
116 | True | VAR-hours Positive | 12.x: (4-byte, Unsigned Value) | 0/0/105 |  |  | T |  |  | R | 3: Low | 116 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 40026 | - | - | 0 |  | -
117 | True | VAR-hours Negative | 12.x: (4-byte, Unsigned Value) | 0/0/106 |  |  | T |  |  | R | 3: Low | 117 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 40028 | - | - | 0 |  | -
118 | True | VA-hours | 13.010: active energy (Wh) | 0/0/107 |  |  | T |  |  | R | 3: Low | 118 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 40030 | - | - | 0 |  | -
119 | True | Neutral Current | 14.019: electric current (A) | 0/0/108 |  |  | T |  |  | R | 3: Low | 119 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40032 | - | - | 0 |  | -
120 | True | Reset Energy Accumulator | 7.x: (2-byte, Unsigned Value) | 0/0/109 |  | U |  |  | W |  | 3: Low | 120 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | - | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 40100 | - | - | 0 |  | -
121 | True | Meter Name ASCII 1 and 2 | 7.x: (2-byte, Unsigned Value) | 0/0/110 |  |  | T |  |  | R | 3: Low | 121 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 1 | - | - | 0 |  | -
122 | True | Meter Name ASCII 3 and 4 | 7.x: (2-byte, Unsigned Value) | 0/0/111 |  |  | T |  |  | R | 3: Low | 122 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 2 | - | - | 0 |  | -
123 | True | Meter Name ASCII 5 and 6 | 7.x: (2-byte, Unsigned Value) | 0/0/112 |  |  | T |  |  | R | 3: Low | 123 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 3 | - | - | 0 |  | -
124 | True | Meter Name ASCII 7 and 8 | 7.x: (2-byte, Unsigned Value) | 0/0/113 |  |  | T |  |  | R | 3: Low | 124 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 4 | - | - | 0 |  | -
125 | True | Meter Name ASCII 9 and 10 | 7.x: (2-byte, Unsigned Value) | 0/0/114 |  |  | T |  |  | R | 3: Low | 125 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 5 | - | - | 0 |  | -
126 | True | Meter Name ASCII 11 and 12 | 7.x: (2-byte, Unsigned Value) | 0/0/115 |  |  | T |  |  | R | 3: Low | 126 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 6 | - | - | 0 |  | -
127 | True | Meter Name ASCII 13 and 14 | 7.x: (2-byte, Unsigned Value) | 0/0/116 |  |  | T |  |  | R | 3: Low | 127 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 7 | - | - | 0 |  | -
128 | True | Meter Name ASCII 15 and 16 | 7.x: (2-byte, Unsigned Value) | 0/0/117 |  |  | T |  |  | R | 3: Low | 128 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 8 | - | - | 0 |  | -
129 | True | Meter Serial Number ASCII 1 and | 7.x: (2-byte, Unsigned Value) | 0/0/118 |  |  | T |  |  | R | 3: Low | 129 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 9 | - | - | 0 |  | -
130 | True | Meter Serial Number ASCII 3 and | 7.x: (2-byte, Unsigned Value) | 0/0/119 |  |  | T |  |  | R | 3: Low | 130 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 10 | - | - | 0 |  | -
131 | True | Meter Serial Number ASCII 5 and | 7.x: (2-byte, Unsigned Value) | 0/0/120 |  |  | T |  |  | R | 3: Low | 131 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 11 | - | - | 0 |  | -
132 | True | Meter Serial Number ASCII 7 and | 7.x: (2-byte, Unsigned Value) | 0/0/121 |  |  | T |  |  | R | 3: Low | 132 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 12 | - | - | 0 |  | -
133 | True | Meter Serial Number ASCII 9 and | 7.x: (2-byte, Unsigned Value) | 0/0/122 |  |  | T |  |  | R | 3: Low | 133 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 13 | - | - | 0 |  | -
134 | True | Meter Serial Number ASCII 11 and | 7.x: (2-byte, Unsigned Value) | 0/0/123 |  |  | T |  |  | R | 3: Low | 134 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 14 | - | - | 0 |  | -
135 | True | Meter Serial Number ASCII 13 and | 7.x: (2-byte, Unsigned Value) | 0/0/124 |  |  | T |  |  | R | 3: Low | 135 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 15 | - | - | 0 |  | -
136 | True | Meter Serial Number ASCII 15 and | 7.x: (2-byte, Unsigned Value) | 0/0/125 |  |  | T |  |  | R | 3: Low | 136 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 16 | - | - | 0 |  | -
137 | True | Meter Type | 7.x: (2-byte, Unsigned Value) | 0/0/126 |  |  | T |  |  | R | 3: Low | 137 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 17 | - | - | 0 |  | -
138 | True | Firmware Version ASCII 1 and 2 | 7.x: (2-byte, Unsigned Value) | 0/0/127 |  |  | T |  |  | R | 3: Low | 138 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 18 | - | - | 0 |  | -
139 | True | Firmware Version ASCII 3 and 4 | 7.x: (2-byte, Unsigned Value) | 0/0/128 |  |  | T |  |  | R | 3: Low | 139 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 19 | - | - | 0 |  | -
140 | True | Map Version | 7.x: (2-byte, Unsigned Value) | 0/0/129 |  |  | T |  |  | R | 3: Low | 140 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 20 | - | - | 0 |  | -
141 | True | Meter Configuration | 7.x: (2-byte, Unsigned Value) | 0/0/130 |  |  | T |  |  | R | 3: Low | 141 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 21 | - | - | 0 |  | -
142 | True | ASIC Version | 7.x: (2-byte, Unsigned Value) | 0/0/131 |  |  | T |  |  | R | 3: Low | 142 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 22 | - | - | 0 |  | -
143 | True | OEM Part Number ASCII 1 and 2 | 7.x: (2-byte, Unsigned Value) | 0/0/132 |  |  | T |  |  | R | 3: Low | 143 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40 | - | - | 0 |  | -
144 | True | OEM Part Number ASCII 3 and 4 | 7.x: (2-byte, Unsigned Value) | 0/0/133 |  |  | T |  |  | R | 3: Low | 144 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 41 | - | - | 0 |  | -
145 | True | OEM Part Number ASCII 5 and 6 | 7.x: (2-byte, Unsigned Value) | 0/0/134 |  |  | T |  |  | R | 3: Low | 145 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 42 | - | - | 0 |  | -
146 | True | OEM Part Number ASCII 7 and 8 | 7.x: (2-byte, Unsigned Value) | 0/0/135 |  |  | T |  |  | R | 3: Low | 146 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 43 | - | - | 0 |  | -
147 | True | OEM Part Number ASCII 9 and 10 | 7.x: (2-byte, Unsigned Value) | 0/0/136 |  |  | T |  |  | R | 3: Low | 147 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 44 | - | - | 0 |  | -
148 | True | OEM Part Number ASCII 11 and 12 | 7.x: (2-byte, Unsigned Value) | 0/0/137 |  |  | T |  |  | R | 3: Low | 148 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 45 | - | - | 0 |  | -
149 | True | OEM Part Number ASCII 13 and 14 | 7.x: (2-byte, Unsigned Value) | 0/0/138 |  |  | T |  |  | R | 3: Low | 149 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 46 | - | - | 0 |  | -
150 | True | OEM Part Number ASCII 15 and 16 | 7.x: (2-byte, Unsigned Value) | 0/0/139 |  |  | T |  |  | R | 3: Low | 150 | RTU // Port B // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 47 | - | - | 0 |  | -

## Conversions
Idx | Description | Type | Param 1 | Param 2 | Param 3 | Param 4
0 | Limit to 0-100 | FILTER | 2 | 4 | 0 | 100
1 | Limit to 0-255 | FILTER | 2 | 4 | 0 | 255
2 | Is not 0 | FILTER | 0 | 1 | 0 | 100
3 | Is higher than 100 | FILTER | 0 | 3 | 100 | 100
4 | Only positive values | FILTER | 2 | 3 | 0 | 100
0 | Celsius to Fahrenheit | ARITH | -1 | 18 | 32 | 0
1 | Fahrenheit to Celsius | ARITH | -3 | 555 | -17.78 | 0
2 | x10 | ARITH | 1 | 1 | 0 | 0
3 | /10 | ARITH | -1 | 1 | 0 | 0
4 | x100 | ARITH | 2 | 1 | 0 | 0
5 | /100 | ARITH | -2 | 1 | 0 | 0
6 | x1000 | ARITH | 3 | 1 | 0 | 0
7 | /1000 | ARITH | -3 | 1 | 0 | 0
8 | 0-100 to 0-255 | SCALE | 0 | 100 | 0 | 255
9 | 0-255 to 0-100 | SCALE | 0 | 255 | 0 | 100
10 | Conversion 0 | ARITH | 0 | 0.1 | 0 | 0