## Signals
Intesis MAPS Excel signals file
PROJECT_NAME | Project1
Intesis MAPS Version | 1.2.26.0
Internal Protocol | BACnet Server
External Protocol | Modbus Master
Timestamp | 2026-01-22
# | Active | Description | Name | Type | Instance | Units | NC | Texts | # States | Rel. Def. | COV | # | Device | # Slave | Base | Read Func | Write Func | Data Length | Format | ByteOrder | Address | Bit | # Bits | Deadband | Conv. Id | Conversions
1 | True |  | Comm Error Device 0 | 3: BI | 0 | -1 | - | - | 2 | - | - | 1 | RTU // Port A // Device 0 | 10 | 0-based | - | - | - | - | - | - | - | - | - |  | -
2 | True |  | Comm Error Device 1 | 3: BI | 1 | -1 | - | - | 2 | - | - | 2 | RTU // Port A // Device 1 | 11 | 0-based | - | - | - | - | - | - | - | - | - |  | -
3 | True |  | Comm Error Device 2 | 3: BI | 2 | -1 | - | - | 2 | - | - | 3 | RTU // Port A // Device 2 | 12 | 0-based | - | - | - | - | - | - | - | - | - |  | -
4 | True |  | Analog Input | 0: AI | 0 | 62 | - | - | - | - | 0 | 4 | RTU // Port A // Device 0 | 10 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 0 | - | - | 0 |  | -
5 | True |  | Analog Output | 1: AO | 0 | 62 | - | - | - | 0 | 0 | 5 | RTU // Port A // Device 0 | 10 | 0-based | - | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 1 | - | - | 0 |  | -
6 | True |  | Analog Value | 2: AV | 0 | 95 | - | - | - | - | 0 | 6 | RTU // Port A // Device 0 | 10 | 0-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 2 | - | - | 0 |  | -
7 | True |  | Binary Input | 3: BI | 3 | -1 | - | - | 2 | - | - | 7 | RTU // Port A // Device 1 | 11 | 0-based | 1: Read Coils | - | 1 | - | - | 0 | - | - | 0 |  | -
8 | True |  | Binary Output | 4: BO | 0 | -1 | - | - | 2 | 0 | - | 8 | RTU // Port A // Device 1 | 11 | 0-based | - | 5: Write Single Coil | 1 | - | - | 1 | - | - | 0 |  | -
9 | True |  | Binary Value | 5: BV | 0 | -1 | - | - | 2 | - | - | 9 | RTU // Port A // Device 1 | 11 | 0-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2 | - | - | 0 |  | -
10 | True |  | Multistate Input | 13: MI | 0 | -1 | - | - | 65535 | - | - | 10 | RTU // Port A // Device 2 | 12 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 0 | - | - | 0 |  | -
11 | True |  | Multistate Output | 14: MO | 0 | -1 | - | - | 65535 | 1 | - | 11 | RTU // Port A // Device 2 | 12 | 0-based | - | 16: Write Multiple Registers | 32 | 0: Unsigned | 0: Big Endian | 2 | - | - | 0 |  | -
12 | True |  | Multistate Value | 19: MV | 0 | -1 | - | - | 65535 | - | - | 12 | RTU // Port A // Device 2 | 12 | 0-based | 3: Read Holding Registers | 16: Write Multiple Registers | 32 | 0: Unsigned | 0: Big Endian | 4 | - | - | 0 |  | -
13 | True |  | Comm Error RTU Port A - GE_EPM2200_Meter_a | 3: BI | 4 | -1 | - | - | 2 | - | - | 13 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | - | - | - | - | - | - | - | - | - |  | -
14 | True | Watts 3-Ph total | Watts 3-Ph total | 0: AI | 1 | 47 | - | - | - | - | 0 | 14 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 900 | - | - | 0 |  | -
15 | True | VARs 3-Ph total | VARs 3-Ph total | 0: AI | 2 | 11 | - | - | - | - | 0 | 15 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 902 | - | - | 0 |  | -
16 | True | VAs 3-Ph total | VAs 3-Ph total | 0: AI | 3 | 8 | - | - | - | - | 0 | 16 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 904 | - | - | 0 |  | -
17 | True | Volts A-N | Volts A-N | 0: AI | 4 | 5 | - | - | - | - | 0 | 17 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1000 | - | - | 0 |  | -
18 | True | Volts B-N | Volts B-N | 0: AI | 5 | 5 | - | - | - | - | 0 | 18 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1002 | - | - | 0 |  | -
19 | True | Volts C-N | Volts C-N | 0: AI | 6 | 5 | - | - | - | - | 0 | 19 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1004 | - | - | 0 |  | -
20 | True | Volts A-B | Volts A-B | 0: AI | 7 | 5 | - | - | - | - | 0 | 20 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1006 | - | - | 0 |  | -
21 | True | Volts B-C | Volts B-C | 0: AI | 8 | 5 | - | - | - | - | 0 | 21 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1008 | - | - | 0 |  | -
22 | True | Volts C-A | Volts C-A | 0: AI | 9 | 5 | - | - | - | - | 0 | 22 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1010 | - | - | 0 |  | -
23 | True | Amps A | Amps A | 0: AI | 10 | 3 | - | - | - | - | 0 | 23 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1012 | - | - | 0 |  | -
24 | True | Amps B | Amps B | 0: AI | 11 | 3 | - | - | - | - | 0 | 24 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1014 | - | - | 0 |  | -
25 | True | Amps C | Amps C | 0: AI | 12 | 3 | - | - | - | - | 0 | 25 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1016 | - | - | 0 |  | -
26 | True | Watts 3-Ph total * | Watts 3-Ph total * | 0: AI | 13 | 47 | - | - | - | - | 0 | 26 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1018 | - | - | 0 |  | -
27 | True | VARs 3-Ph total * | VARs 3-Ph total * | 0: AI | 14 | 11 | - | - | - | - | 0 | 27 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1020 | - | - | 0 |  | -
28 | True | VAs 3-Ph total * | VAs 3-Ph total * | 0: AI | 15 | 8 | - | - | - | - | 0 | 28 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1022 | - | - | 0 |  | -
29 | True | Power Factor 3-Ph total | Power Factor 3-Ph total | 0: AI | 16 | 15 | - | - | - | - | 0 | 29 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1024 | - | - | 0 |  | -
30 | True | Frequency | Frequency | 0: AI | 17 | 27 | - | - | - | - | 0 | 30 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1026 | - | - | 0 |  | -
31 | True | Neutral Current | Neutral Current | 0: AI | 18 | 3 | - | - | - | - | 0 | 31 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 1028 | - | - | 0 |  | -
32 | True | W-hours Received | W-hours Received | 0: AI | 19 | 95 | - | - | - | - | 0 | 32 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1100 | - | - | 0 |  | -
33 | True | W-hours Delivered | W-hours Delivered | 0: AI | 20 | 95 | - | - | - | - | 0 | 33 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1102 | - | - | 0 |  | -
34 | True | W-hours Net | W-hours Net | 0: AI | 21 | 95 | - | - | - | - | 0 | 34 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1104 | - | - | 0 |  | -
35 | True | W-hours Total | W-hours Total | 0: AI | 22 | 95 | - | - | - | - | 0 | 35 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1106 | - | - | 0 |  | -
36 | True | VAR-hours Positive | VAR-hours Positive | 0: AI | 23 | 95 | - | - | - | - | 0 | 36 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1108 | - | - | 0 |  | -
37 | True | VAR-hours Negative | VAR-hours Negative | 0: AI | 24 | 95 | - | - | - | - | 0 | 37 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1110 | - | - | 0 |  | -
38 | True | VAR-hours Net | VAR-hours Net | 0: AI | 25 | 95 | - | - | - | - | 0 | 38 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1112 | - | - | 0 |  | -
39 | True | VAR-hours Total | VAR-hours Total | 0: AI | 26 | 95 | - | - | - | - | 0 | 39 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1114 | - | - | 0 |  | -
40 | True | VA-hours Total | VA-hours Total | 0: AI | 27 | 95 | - | - | - | - | 0 | 40 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 1: Signed (C2) | 0: Big Endian | 1116 | - | - | 0 |  | -
41 | True | Amps A Average | Amps A Average | 0: AI | 28 | 3 | - | - | - | - | 0 | 41 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2000 | - | - | 0 |  | -
42 | True | Amps B Average | Amps B Average | 0: AI | 29 | 3 | - | - | - | - | 0 | 42 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2002 | - | - | 0 |  | -
43 | True | Amps C Average | Amps C Average | 0: AI | 30 | 3 | - | - | - | - | 0 | 43 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2004 | - | - | 0 |  | -
44 | True | Positive Watts 3-Ph average | Positive Watts 3-Ph average | 0: AI | 31 | 47 | - | - | - | - | 0 | 44 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2006 | - | - | 0 |  | -
45 | True | Positive VARs 3-Ph average | Positive VARs 3-Ph average | 0: AI | 32 | 11 | - | - | - | - | 0 | 45 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2008 | - | - | 0 |  | -
46 | True | Negative Watts 3-Ph average | Negative Watts 3-Ph average | 0: AI | 33 | 47 | - | - | - | - | 0 | 46 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2010 | - | - | 0 |  | -
47 | True | Negative VARs 3-Ph average | Negative VARs 3-Ph average | 0: AI | 34 | 11 | - | - | - | - | 0 | 47 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2012 | - | - | 0 |  | -
48 | True | VAs 3-Ph Average | VAs 3-Ph Average | 0: AI | 35 | 8 | - | - | - | - | 0 | 48 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2014 | - | - | 0 |  | -
49 | True | Positive PF 3-Ph average | Positive PF 3-Ph average | 0: AI | 36 | 15 | - | - | - | - | 0 | 49 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2016 | - | - | 0 |  | -
50 | True | Negative PF 3-PF average | Negative PF 3-PF average | 0: AI | 37 | 15 | - | - | - | - | 0 | 50 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 2018 | - | - | 0 |  | -
51 | True | Volts A-N Minimum | Volts A-N Minimum | 0: AI | 38 | 5 | - | - | - | - | 0 | 51 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3000 | - | - | 0 |  | -
52 | True | Volts B-N Minimum | Volts B-N Minimum | 0: AI | 39 | 5 | - | - | - | - | 0 | 52 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3002 | - | - | 0 |  | -
53 | True | Volts C-N Minimum | Volts C-N Minimum | 0: AI | 40 | 5 | - | - | - | - | 0 | 53 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3004 | - | - | 0 |  | -
54 | True | Volts A-B Minimum | Volts A-B Minimum | 0: AI | 41 | 5 | - | - | - | - | 0 | 54 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3006 | - | - | 0 |  | -
55 | True | Volts B-C Minimum | Volts B-C Minimum | 0: AI | 42 | 5 | - | - | - | - | 0 | 55 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3008 | - | - | 0 |  | -
56 | True | Volts C-A Minimum | Volts C-A Minimum | 0: AI | 43 | 5 | - | - | - | - | 0 | 56 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3010 | - | - | 0 |  | -
57 | True | Amps A Minimum Avg demand | Amps A Minimum Avg demand | 0: AI | 44 | 3 | - | - | - | - | 0 | 57 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3012 | - | - | 0 |  | -
58 | True | Amps B Minimum Avg demand | Amps B Minimum Avg demand | 0: AI | 45 | 3 | - | - | - | - | 0 | 58 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3014 | - | - | 0 |  | -
59 | True | Amps C Minimum Avg demand | Amps C Minimum Avg demand | 0: AI | 46 | 3 | - | - | - | - | 0 | 59 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3016 | - | - | 0 |  | -
60 | True | Positive Watts 3-Ph Minimum Average Demand | Positive Watts 3-Ph Minimum Ave | 0: AI | 47 | 47 | - | - | - | - | 0 | 60 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3018 | - | - | 0 |  | -
61 | True | Positive VARs 3-Ph Minimum Average Demand | Positive VARs 3-Ph Minimum Aver | 0: AI | 48 | 11 | - | - | - | - | 0 | 61 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3020 | - | - | 0 |  | -
62 | True | Negative Watts 3-Ph Minimum Average Demand | Negative Watts 3-Ph Minimum Ave | 0: AI | 49 | 47 | - | - | - | - | 0 | 62 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3022 | - | - | 0 |  | -
63 | True | Negative VARs 3-Ph Minimum Average Demand | Negative VARs 3-Ph Minimum Aver | 0: AI | 50 | 11 | - | - | - | - | 0 | 63 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3024 | - | - | 0 |  | -
64 | True | VAs 3-Ph Minimum Avg Demand | VAs 3-Ph Minimum Avg Demand | 0: AI | 51 | 8 | - | - | - | - | 0 | 64 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3026 | - | - | 0 |  | -
65 | True | Positive Power Factor 3-Ph Minimum Avg Demand | Positive Power Factor 3-Ph Mini | 0: AI | 52 | 15 | - | - | - | - | 0 | 65 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3028 | - | - | 0 |  | -
66 | True | Negative Power Factor 3-Ph Minimum Avg Demand | Negative Power Factor 3-Ph Mini | 0: AI | 53 | 15 | - | - | - | - | 0 | 66 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3030 | - | - | 0 |  | -
67 | True | Frequency Minimum | Frequency Minimum | 0: AI | 54 | 27 | - | - | - | - | 0 | 67 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3032 | - | - | 0 |  | -
68 | True | Volts A-N Maximum | Volts A-N Maximum | 0: AI | 55 | 5 | - | - | - | - | 0 | 68 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3100 | - | - | 0 |  | -
69 | True | Volts B-N Maximum | Volts B-N Maximum | 0: AI | 56 | 5 | - | - | - | - | 0 | 69 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3102 | - | - | 0 |  | -
70 | True | Volts C-N Maximum | Volts C-N Maximum | 0: AI | 57 | 5 | - | - | - | - | 0 | 70 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3104 | - | - | 0 |  | -
71 | True | Volts A-B Maximum | Volts A-B Maximum | 0: AI | 58 | 5 | - | - | - | - | 0 | 71 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3106 | - | - | 0 |  | -
72 | True | Volts B-C Maximum | Volts B-C Maximum | 0: AI | 59 | 5 | - | - | - | - | 0 | 72 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3108 | - | - | 0 |  | -
73 | True | Volts C-A Maximum | Volts C-A Maximum | 0: AI | 60 | 5 | - | - | - | - | 0 | 73 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3110 | - | - | 0 |  | -
74 | True | Amps A Maximum Avg demand | Amps A Maximum Avg demand | 0: AI | 61 | 3 | - | - | - | - | 0 | 74 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3112 | - | - | 0 |  | -
75 | True | Amps B Maximum Avg demand | Amps B Maximum Avg demand | 0: AI | 62 | 3 | - | - | - | - | 0 | 75 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3114 | - | - | 0 |  | -
76 | True | Amps C Maximum Avg demand | Amps C Maximum Avg demand | 0: AI | 63 | 3 | - | - | - | - | 0 | 76 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3116 | - | - | 0 |  | -
77 | True | Positive Watts 3-Ph Maximum Avg demand | Positive Watts 3-Ph Maximum Avg | 0: AI | 64 | 47 | - | - | - | - | 0 | 77 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3118 | - | - | 0 |  | -
78 | True | Positive VARs 3-Ph Maximum Avg demand | Positive VARs 3-Ph Maximum Avg | 0: AI | 65 | 11 | - | - | - | - | 0 | 78 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3120 | - | - | 0 |  | -
79 | True | Negative Watts 3-Ph Maximum Avg demand | Negative Watts 3-Ph Maximum Avg | 0: AI | 66 | 47 | - | - | - | - | 0 | 79 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3122 | - | - | 0 |  | -
80 | True | Negative VARs 3-Ph Maximum Avg demand | Negative VARs 3-Ph Maximum Avg | 0: AI | 67 | 11 | - | - | - | - | 0 | 80 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3124 | - | - | 0 |  | -
81 | True | VAs 3-Ph Maximum Avg Demand | VAs 3-Ph Maximum Avg Demand | 0: AI | 68 | 8 | - | - | - | - | 0 | 81 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3126 | - | - | 0 |  | -
82 | True | Positive Power Factor 3-Ph Maximum Avg Demand | Positive Power Factor 3-Ph Maxi | 0: AI | 69 | 15 | - | - | - | - | 0 | 82 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3128 | - | - | 0 |  | -
83 | True | Negative Power Factor 3-Ph Maximum Avg demand | Negative Power Factor 3-Ph Maxi | 0: AI | 70 | 15 | - | - | - | - | 0 | 83 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3130 | - | - | 0 |  | -
84 | True | Frequency Maximum | Frequency Maximum | 0: AI | 71 | 27 | - | - | - | - | 0 | 84 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 3: Float | 0: Big Endian | 3132 | - | - | 0 |  | -
85 | True | Phase A Current | Phase A Current | 0: AI | 72 | 14 | - | - | - | - | 0 | 85 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4100 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
86 | True | Phase B Current | Phase B Current | 0: AI | 73 | 14 | - | - | - | - | 0 | 86 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4101 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
87 | True | Phase C Current | Phase C Current | 0: AI | 74 | 14 | - | - | - | - | 0 | 87 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4102 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
88 | True | Angle Volts A-B | Angle Volts A-B | 0: AI | 75 | 14 | - | - | - | - | 0 | 88 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4103 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
89 | True | Angle Volts B-C | Angle Volts B-C | 0: AI | 76 | 14 | - | - | - | - | 0 | 89 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4104 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
90 | True | Angle Volts C-A | Angle Volts C-A | 0: AI | 77 | 14 | - | - | - | - | 0 | 90 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 1: Signed (C2) | 0: Big Endian | 4105 | - | - | 0 | DIRECTION[<]:INDEXES[-;-;10;-] | Enabled
91 | True | Meter Status | Meter Status | 0: AI | 78 | 95 | - | - | - | - | 0 | 91 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 5000 | - | - | 0 |  | -
92 | True | Time Since Reset | Time Since Reset | 0: AI | 79 | 95 | - | - | - | - | 0 | 92 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 5002 | - | - | 0 |  | -
93 | True | System Sanity Indicator | System Sanity Indicator | 0: AI | 80 | 95 | - | - | - | - | 0 | 93 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40001 | - | - | 0 |  | -
94 | True | Volts A-N * | Volts A-N * | 0: AI | 81 | 5 | - | - | - | - | 0 | 94 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40002 | - | - | 0 |  | -
95 | True | Volts B-N * | Volts B-N * | 0: AI | 82 | 5 | - | - | - | - | 0 | 95 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40003 | - | - | 0 |  | -
96 | True | Volts C-N * | Volts C-N * | 0: AI | 83 | 5 | - | - | - | - | 0 | 96 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40004 | - | - | 0 |  | -
97 | True | Amps A * | Amps A * | 0: AI | 84 | 3 | - | - | - | - | 0 | 97 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40005 | - | - | 0 |  | -
98 | True | Amps B * | Amps B * | 0: AI | 85 | 3 | - | - | - | - | 0 | 98 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40006 | - | - | 0 |  | -
99 | True | Amps C * | Amps C * | 0: AI | 86 | 3 | - | - | - | - | 0 | 99 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40007 | - | - | 0 |  | -
100 | True | Watts 3-Ph total * | Watts 3-Ph total * | 0: AI | 87 | 47 | - | - | - | - | 0 | 100 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40008 | - | - | 0 |  | -
101 | True | VARs 3-Ph total * | VARs 3-Ph total * | 0: AI | 88 | 11 | - | - | - | - | 0 | 101 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40009 | - | - | 0 |  | -
102 | True | VAs 3-Ph total * | VAs 3-Ph total * | 0: AI | 89 | 8 | - | - | - | - | 0 | 102 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40010 | - | - | 0 |  | -
103 | True | Power Factor 3-Ph Total | Power Factor 3-Ph Total | 0: AI | 90 | 15 | - | - | - | - | 0 | 103 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40011 | - | - | 0 |  | -
104 | True | Frequency * | Frequency * | 0: AI | 91 | 27 | - | - | - | - | 0 | 104 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40012 | - | - | 0 |  | -
105 | True | Volts A-B * | Volts A-B * | 0: AI | 92 | 5 | - | - | - | - | 0 | 105 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40013 | - | - | 0 |  | -
106 | True | Volts B-C * | Volts B-C * | 0: AI | 93 | 5 | - | - | - | - | 0 | 106 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40014 | - | - | 0 |  | -
107 | True | Volts C-A * | Volts C-A * | 0: AI | 94 | 5 | - | - | - | - | 0 | 107 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40015 | - | - | 0 |  | -
108 | True | CT numerator | CT numerator | 0: AI | 95 | 95 | - | - | - | - | 0 | 108 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40016 | - | - | 0 |  | -
109 | True | CT multiplier | CT multiplier | 0: AI | 96 | 95 | - | - | - | - | 0 | 109 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40017 | - | - | 0 |  | -
110 | True | CT denominator | CT denominator | 0: AI | 97 | 95 | - | - | - | - | 0 | 110 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40018 | - | - | 0 |  | -
111 | True | PT numerator | PT numerator | 0: AI | 98 | 95 | - | - | - | - | 0 | 111 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40019 | - | - | 0 |  | -
112 | True | PT multiplier | PT multiplier | 0: AI | 99 | 95 | - | - | - | - | 0 | 112 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40020 | - | - | 0 |  | -
113 | True | PT denominator | PT denominator | 0: AI | 100 | 95 | - | - | - | - | 0 | 113 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40021 | - | - | 0 |  | -
114 | True | W-hours Positive | W-hours Positive | 0: AI | 101 | 18 | - | - | - | - | 0 | 114 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 40022 | - | - | 0 |  | -
115 | True | W-hours Negative | W-hours Negative | 0: AI | 102 | 18 | - | - | - | - | 0 | 115 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 40024 | - | - | 0 |  | -
116 | True | VAR-hours Positive | VAR-hours Positive | 0: AI | 103 | 203 | - | - | - | - | 0 | 116 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 40026 | - | - | 0 |  | -
117 | True | VAR-hours Negative | VAR-hours Negative | 0: AI | 104 | 203 | - | - | - | - | 0 | 117 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 40028 | - | - | 0 |  | -
118 | True | VA-hours | VA-hours | 0: AI | 105 | 18 | - | - | - | - | 0 | 118 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 40030 | - | - | 0 |  | -
119 | True | Neutral Current | Neutral Current | 0: AI | 106 | 3 | - | - | - | - | 0 | 119 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40032 | - | - | 0 |  | -
120 | True | Reset Energy Accumulator | Reset Energy Accumulator | 1: AO | 1 | 95 | - | - | - | 0 | 0 | 120 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | - | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 40100 | - | - | 0 |  | -
121 | True | Meter Name ASCII 1 and 2 | Meter Name ASCII 1 and 2 | 0: AI | 107 | 95 | - | - | - | - | 0 | 121 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 1 | - | - | 0 |  | -
122 | True | Meter Name ASCII 3 and 4 | Meter Name ASCII 3 and 4 | 0: AI | 108 | 95 | - | - | - | - | 0 | 122 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 2 | - | - | 0 |  | -
123 | True | Meter Name ASCII 5 and 6 | Meter Name ASCII 5 and 6 | 0: AI | 109 | 95 | - | - | - | - | 0 | 123 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 3 | - | - | 0 |  | -
124 | True | Meter Name ASCII 7 and 8 | Meter Name ASCII 7 and 8 | 0: AI | 110 | 95 | - | - | - | - | 0 | 124 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 4 | - | - | 0 |  | -
125 | True | Meter Name ASCII 9 and 10 | Meter Name ASCII 9 and 10 | 0: AI | 111 | 95 | - | - | - | - | 0 | 125 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 5 | - | - | 0 |  | -
126 | True | Meter Name ASCII 11 and 12 | Meter Name ASCII 11 and 12 | 0: AI | 112 | 95 | - | - | - | - | 0 | 126 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 6 | - | - | 0 |  | -
127 | True | Meter Name ASCII 13 and 14 | Meter Name ASCII 13 and 14 | 0: AI | 113 | 95 | - | - | - | - | 0 | 127 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 7 | - | - | 0 |  | -
128 | True | Meter Name ASCII 15 and 16 | Meter Name ASCII 15 and 16 | 0: AI | 114 | 95 | - | - | - | - | 0 | 128 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 8 | - | - | 0 |  | -
129 | True | Meter Serial Number ASCII 1 and 2 | Meter Serial Number ASCII 1 and | 0: AI | 115 | 95 | - | - | - | - | 0 | 129 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 9 | - | - | 0 |  | -
130 | True | Meter Serial Number ASCII 3 and 4 | Meter Serial Number ASCII 3 and | 0: AI | 116 | 95 | - | - | - | - | 0 | 130 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 10 | - | - | 0 |  | -
131 | True | Meter Serial Number ASCII 5 and 6 | Meter Serial Number ASCII 5 and | 0: AI | 117 | 95 | - | - | - | - | 0 | 131 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 11 | - | - | 0 |  | -
132 | True | Meter Serial Number ASCII 7 and 8 | Meter Serial Number ASCII 7 and | 0: AI | 118 | 95 | - | - | - | - | 0 | 132 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 12 | - | - | 0 |  | -
133 | True | Meter Serial Number ASCII 9 and 10 | Meter Serial Number ASCII 9 and | 0: AI | 119 | 95 | - | - | - | - | 0 | 133 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 13 | - | - | 0 |  | -
134 | True | Meter Serial Number ASCII 11 and 12 | Meter Serial Number ASCII 11 and | 0: AI | 120 | 95 | - | - | - | - | 0 | 134 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 14 | - | - | 0 |  | -
135 | True | Meter Serial Number ASCII 13 and 14 | Meter Serial Number ASCII 13 and | 0: AI | 121 | 95 | - | - | - | - | 0 | 135 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 15 | - | - | 0 |  | -
136 | True | Meter Serial Number ASCII 15 and 16 | Meter Serial Number ASCII 15 and | 0: AI | 122 | 95 | - | - | - | - | 0 | 136 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 16 | - | - | 0 |  | -
137 | True | Meter Type | Meter Type | 0: AI | 123 | 95 | - | - | - | - | 0 | 137 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 17 | - | - | 0 |  | -
138 | True | Firmware Version ASCII 1 and 2 | Firmware Version ASCII 1 and 2 | 0: AI | 124 | 95 | - | - | - | - | 0 | 138 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 18 | - | - | 0 |  | -
139 | True | Firmware Version ASCII 3 and 4 | Firmware Version ASCII 3 and 4 | 0: AI | 125 | 95 | - | - | - | - | 0 | 139 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 19 | - | - | 0 |  | -
140 | True | Map Version | Map Version | 0: AI | 126 | 95 | - | - | - | - | 0 | 140 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 20 | - | - | 0 |  | -
141 | True | Meter Configuration | Meter Configuration | 0: AI | 127 | 95 | - | - | - | - | 0 | 141 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 21 | - | - | 0 |  | -
142 | True | ASIC Version | ASIC Version | 0: AI | 128 | 95 | - | - | - | - | 0 | 142 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 22 | - | - | 0 |  | -
143 | True | OEM Part Number ASCII 1 and 2 | OEM Part Number ASCII 1 and 2 | 0: AI | 129 | 95 | - | - | - | - | 0 | 143 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 40 | - | - | 0 |  | -
144 | True | OEM Part Number ASCII 3 and 4 | OEM Part Number ASCII 3 and 4 | 0: AI | 130 | 95 | - | - | - | - | 0 | 144 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 41 | - | - | 0 |  | -
145 | True | OEM Part Number ASCII 5 and 6 | OEM Part Number ASCII 5 and 6 | 0: AI | 131 | 95 | - | - | - | - | 0 | 145 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 42 | - | - | 0 |  | -
146 | True | OEM Part Number ASCII 7 and 8 | OEM Part Number ASCII 7 and 8 | 0: AI | 132 | 95 | - | - | - | - | 0 | 146 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 43 | - | - | 0 |  | -
147 | True | OEM Part Number ASCII 9 and 10 | OEM Part Number ASCII 9 and 10 | 0: AI | 133 | 95 | - | - | - | - | 0 | 147 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 44 | - | - | 0 |  | -
148 | True | OEM Part Number ASCII 11 and 12 | OEM Part Number ASCII 11 and 12 | 0: AI | 134 | 95 | - | - | - | - | 0 | 148 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 45 | - | - | 0 |  | -
149 | True | OEM Part Number ASCII 13 and 14 | OEM Part Number ASCII 13 and 14 | 0: AI | 135 | 95 | - | - | - | - | 0 | 149 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 46 | - | - | 0 |  | -
150 | True | OEM Part Number ASCII 15 and 16 | OEM Part Number ASCII 15 and 16 | 0: AI | 136 | 95 | - | - | - | - | 0 | 150 | RTU // Port A // GE_EPM2200_Meter_a | 1 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 47 | - | - | 0 |  | -

## BACnet Server
Units
-
ampere_square_meters (169)
amperes (3)
amperes_per_meter (167)
amperes_per_square_meter (168)
bars (55)
becquerels (222)
btus (20)
btus_per_hour (50)
btus_per_pound (117)
btus_per_pound_dry_air (24)
centimeters(118)
meters (31)
centimeters_of_mercury (60)
centimeters_of_water (57)
cubic_feet (79)
cubic_feet_per_hour (191)
cubic_feet_per_minute (84)
cubic_feet_per_second (142)
cubic_meters (80)
cubic_meters_per_hour (135)
cubic_meters_per_minute (165)
cubic_meters_per_second (85)
currency1 (105)
currency10 (114)
currency2 (106)
currency3 (107)
currency4 (108)
currency5 (109)
currency6 (110)
currency7 (111)
currency8 (112)
currency9 (113)
cycles_per_hour (25)
cycles_per_minute (26)
days (70)
decibels (199)
decibels_a (232)
decibels_millivolt (200)
decibels_volt (201)
degree_days_Celsius (65)
degree_days_Fahrenheit (66)
degrees_angular (90)
degrees_Celsius (62)
degrees_Celsius_per_hour (91)
degrees_Celsius_per_minute (92)
degrees_Fahrenheit (64)
degrees_Fahrenheit_per_hour (93)
degrees_Fahrenheit_per_minute (94)
degrees_Kelvin (63)
degrees_Kelvin_per_hour (181)
degrees_Kelvin_per_minute (182)
degrees_phase (14)
delta_degrees_Fahrenheit (120)
delta_degrees_Kelvin (121)
farads (170)
feet(33)
candelas_per_square_meter (180)
feet_per_minute (77)
feet_per_second (76)
grams_of_water_per_kilogram_dry_air(28)
micrometers (194)
grams_per_cubic_centimeter (221)
grams_per_cubic_meter (217)
grams_per_gram (208)
grams_per_kilogram (210)
grams_per_liter (214)
grams_per_milliliter (213)
grams_per_square_meter (235)
gray (225)
hectopascals (133)
henrys (171)
hertz (27)
horsepower (51)
hours (71)
hundredths_seconds (158)
imperial_gallons (81)
imperial_gallons_per_minute (86)
inches_of_mercury (61)
inches_of_water (58)
joule_seconds (183)
joules (16)
joules_per_degree_Kelvin (127)
joules_per_kilogram_degree_Kelvin (128)
joules_per_kilogram_dry_air (23)
kilo_btus (147)
kilo_btus_per_hour (157)
kilobecquerels (223)
kilograms_per_cubic_meter (186)
kilograms_per_hour (44)
kilograms_per_kilogram (209)
kilograms_per_minute (43)
kilograms_per_second (42)
kilohertz (129)
kilohms (122)
kilojoules (17)
kilojoules_per_degree_Kelvin (151)
kilojoules_per_kilogram (125)
kilojoules_per_kilogram_dry_air (149)
kilometers_per_hour (75)
kilopascals (54)
kilovolt_amperes (9)
kilovolt_amperes_reactive (12)
kilovolts (6)
kilowatt_hours (19)
kilowatt_hours_per_square_foot (138)
kilowatt_hours_per_square_meter (137)
kilowatt_hours_reactive (204)
kilowatts (48)
liters (82)
liters_per_hour (136)
liters_per_minute (88)
liters_per_second (87)
mega_btus (148)
megabecquerels (224)
megahertz (130)
megajoules (126)
megajoules_per_degree_Kelvin (152)
megajoules_per_kilogram_dry_air (150)
megajoules_per_square_foot (140)
megajoules_per_square_meter (139)
megavolt_amperes (10)
megavolt_amperes_reactive (13)
megavolts (7)
megawatt_hours (146)
megawatt_hours_reactive (205)
megawatts (49)
megohms (123)
meters_per_hour (164)
meters_per_minute (163)
meters_per_second (74)
micrograms_per_cubic_meter (219)
micrograms_per_liter (216)
microgray (227)
microsiemens (190)
microsieverts (230)
microsieverts_per_hour (231)
miles_per_hour (78)
milliamperes (2)
millibars (134)
milligrams(196)
kilograms (39)
milligrams_per_cubic_meter (218)
milligrams_per_gram (211)
milligrams_per_kilogram (212)
milligrams_per_liter (215)
milligray (226)
milliliters (197)
milliliters_per_second (198)
millimeters_of_mercury (59)
millimeters_of_water (206)
millimeters_per_minute (162)
millimeters_per_second (161)
milliohms (145)
milliseconds (159)
millisiemens (202)
millisieverts (229)
millivolts (124)
milliwatts (132)
minutes (72)
minutes_per_degree_kelvin (236)
months (68)
nanograms_per_cubic_meter (220)
nephelometric_turbidity_unit (233)
newton (153)
newton_meters (160)
newton_seconds (187)
newtons_per_meter (188)
no_units (95)
ohm_meters (172)
ohms (4)
parts_per_billion (97)
parts_per_million (96)
pascals (53)
per_mille (207)
per_minute (100)
per_second (101)
percent (98)
percent_obscuration_per_foot (143)
percent_obscuration_per_meter (144)
percent_per_second (99)
pH (234)
pounds_force_per_square_inch (56)
pounds_mass_per_hour (46)
pounds_mass_per_minute (45)
pounds_mass_per_second (119)
power_factor (15)
psi_per_degree_Fahrenheit (102)
radians (103)
radians_per_second (184)
revolutions_per_minute (104)
seconds (73)
siemens (173)
siemens_per_meter (174)
sieverts (228)
square_centimeters (116)
square_feet (1)
square_inches (115)
square_meters (0)
square_meters_per_Newton (185)
teslas (175)
therms (21)
ton_hours (22)
tons (41)
grams_per_minute (155)
tons_per_hour (156)
tons_refrigeration (52)
us_gallons (83)
us_gallons_per_hour (192)
us_gallons_per_minute (89)
VAh (239)
volt_amperes (8)
volt_amperes_reactive (11)
volts (5)
volts_per_degree_Kelvin (176)
volts_per_meter (177)
watt_hours (18)
watt_hours_reactive (203)
watts (47)
watts_per_meter_per_degree_Kelvin (189)
watts_per_square_meter (35)
luxes (37)
watts_per_square_meter_degree_kelvin (141)
webers (178)
weeks (69)
years (67)

## Conversions
Idx | Description | Type | Param 1 | Param 2 | Param 3 | Param 4
0 | Limit to 0-100 | FILTER | 2 | 4 | 0 | 100
1 | Limit to 0-255 | FILTER | 2 | 4 | 0 | 255
2 | Is not 0 | FILTER | 0 | 1 | 0 | 100
3 | Is higher than 100 | FILTER | 0 | 3 | 100 | 100
4 | Only positive values | FILTER | 2 | 3 | 0 | 100
0 | Celsius to Fahrenheit | ARITH | -1 | 18 | 32 | 0
1 | Fahrenheit to Celsius | ARITH | -3 | 555 | -17.78 | 0
2 | x10 | ARITH | 1 | 1 | 0 | 0
3 | /10 | ARITH | -1 | 1 | 0 | 0
4 | x100 | ARITH | 2 | 1 | 0 | 0
5 | /100 | ARITH | -2 | 1 | 0 | 0
6 | x1000 | ARITH | 3 | 1 | 0 | 0
7 | /1000 | ARITH | -3 | 1 | 0 | 0
8 | 0-100 to 0-255 | SCALE | 0 | 100 | 0 | 255
9 | 0-255 to 0-100 | SCALE | 0 | 255 | 0 | 100
10 | Conversion 0 | ARITH | 0 | 0.1 | 0 | 0