## Signals
Intesis MAPS Excel signals file
PROJECT_NAME | Project1
Intesis MAPS Version | 1.2.23.0
Internal Protocol | KNX
External Protocol | Modbus Master
Timestamp | 2026-01-09
# | Active | Description | DPT | Group Address | Additional Addresses | U | T | Ri | W | R | Priority | # | Device | # Slave | Base | Read Func | Write Func | Data Length | Format | ByteOrder | Address | Bit | # Bits | Deadband | Conv. Id | Conversions
1 | True | Comm Error Device 0 | 1.005: alarm | 0/0/100 |  |  | T |  |  | R | 3: Low | 1 | RTU // Port B // Device 0 | 10 | 0-based | - | - | - | - | - | - | - | - | - |  | -
2 | True | Comm Error Device 1 | 1.005: alarm | 0/0/101 |  |  | T |  |  | R | 3: Low | 2 | RTU // Port B // Device 1 | 11 | 0-based | - | - | - | - | - | - | - | - | - |  | -
3 | True | Comm Error Device 2 | 1.005: alarm | 0/0/102 |  |  | T |  |  | R | 3: Low | 3 | RTU // Port B // Device 2 | 12 | 0-based | - | - | - | - | - | - | - | - | - |  | -
4 | True | On_Off_R | 1.001: switch | 0/0/1 |  |  | T |  |  | R | 3: Low | 4 | RTU // Port B // Device 0 | 10 | 0-based | 1: Read Coils | - | 1 | - | - | 0 | - | - | 0 |  | -
5 | True | On_Off_W | 1.001: switch | 0/0/2 |  | U |  |  | W |  | 3: Low | 5 | RTU // Port B // Device 0 | 10 | 0-based | - | 5: Write Single Coil | 1 | - | - | 1 | - | - | 0 |  | -
6 | True | On_Off_RW | 1.001: switch | 0/0/3 |  | U | T |  | W | R | 3: Low | 6 | RTU // Port B // Device 0 | 10 | 0-based | 1: Read Coils | 5: Write Single Coil | 1 | - | - | 2 | - | - | 0 |  | -
7 | True | Temp_R | 9.001: temperature (ºC) | 0/0/4 |  |  | T |  |  | R | 3: Low | 7 | RTU // Port B // Device 1 | 11 | 0-based | 3: Read Holding Registers | - | 16 | 0: Unsigned | 0: Big Endian | 0 | - | - | 0 |  | -
8 | True | Temp_W | 9.001: temperature (ºC) | 0/0/5 |  | U |  |  | W |  | 3: Low | 8 | RTU // Port B // Device 1 | 11 | 0-based | - | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 1 | - | - | 0 |  | -
9 | True | Temp_RW | 9.001: temperature (ºC) | 0/0/6 |  | U | T |  | W | R | 3: Low | 9 | RTU // Port B // Device 1 | 11 | 0-based | 3: Read Holding Registers | 6: Write Single Register | 16 | 0: Unsigned | 0: Big Endian | 2 | - | - | 0 |  | -
10 | True | Counter_R | 5.010: counter pulses (0..255) | 0/0/7 |  |  | T |  |  | R | 3: Low | 10 | RTU // Port B // Device 2 | 12 | 0-based | 3: Read Holding Registers | - | 32 | 0: Unsigned | 0: Big Endian | 0 | - | - | 0 |  | -
11 | True | Counter_W | 5.010: counter pulses (0..255) | 0/0/8 |  | U |  |  | W |  | 3: Low | 11 | RTU // Port B // Device 2 | 12 | 0-based | - | 16: Write Multiple Registers | 32 | 0: Unsigned | 0: Big Endian | 2 | - | - | 0 |  | -
12 | True | Counter_RW | 5.010: counter pulses (0..255) | 0/0/9 |  | U | T |  | W | R | 3: Low | 12 | RTU // Port B // Device 2 | 12 | 0-based | 3: Read Holding Registers | 16: Write Multiple Registers | 32 | 0: Unsigned | 0: Big Endian | 4 | - | - | 0 |  | -

## Conversions
Idx | Description | Type | Param 1 | Param 2 | Param 3 | Param 4
0 | Limit to 0-100 | FILTER | 2 | 4 | 0 | 100
1 | Limit to 0-255 | FILTER | 2 | 4 | 0 | 255
2 | Is not 0 | FILTER | 0 | 1 | 0 | 100
3 | Is higher than 100 | FILTER | 0 | 3 | 100 | 100
4 | Only positive values | FILTER | 2 | 3 | 0 | 100
0 | Celsius to Fahrenheit | ARITH | -1 | 18 | 32 | 0
1 | Fahrenheit to Celsius | ARITH | -3 | 555 | -17.78 | 0
2 | x10 | ARITH | 1 | 1 | 0 | 0
3 | /10 | ARITH | -1 | 1 | 0 | 0
4 | x100 | ARITH | 2 | 1 | 0 | 0
5 | /100 | ARITH | -2 | 1 | 0 | 0
6 | x1000 | ARITH | 3 | 1 | 0 | 0
7 | /1000 | ARITH | -3 | 1 | 0 | 0
8 | 0-100 to 0-255 | SCALE | 0 | 100 | 0 | 255
9 | 0-255 to 0-100 | SCALE | 0 | 255 | 0 | 100